## Setting
Sl.No. | User Name | Design Name | Description | Minimum | Maximum | Scaling Factor | Data Type | Unit
1 | EnableOperModeSelect | EnableOperModeSelect | Enable or disables the operation mode selector function. 1 for enabling and 0 for disabling. | 0 | 1 | 1 | Boolean | NA
2 | SoCMin | SoCMin | Minimum value of usable SoC of the battery energy storage system. | 0 | 100 | 1 | real | % (NA)
3 | SoCMax | SoCMax | Maximum value of usable SoC of the battery energy storage system. | 0 | 100 | 1 | real | % (NA)
4 | BattCap | BattCap | Usable energy capacity of the battery energy storage system. | 0 | 100000 | 1 | real | kW
5 | InvAppPow | InvAppPow | Apparent power rating of the inverter. | 0 | 100000 | 1 | real | kVA
6 | EnablePreProcessing | EnablePreProcessing | Enables or disables the pre-processing functionality. 1 for enabling and 0 for disabling. | 0 | 1 | 1 | Boolean | NA
7 | MaxDischargingPow | MaxDischargingPow | Maximum value of active power allowed while discharging. | 1 | 100000 | 1 | real | kW
8 | MaxChargingPow | MaxChargingPow | Maximum value of reactive power allowed while discharging. | 1 | 100000 | 1 | real | kW
9 | ActvPowMeasRefPoint | ActvPowMeasRefPoint | Reference for the active power measurement to be achieved. | 1 | 100000 | 1 | real | kW
10 | ReactvPowMeasRefPoint | ReactvPowMeasRefPoint | Reference for the reactive power measurement to be achieved. | 1 | 100000 | 1 | real | kW
11 | RefFreq | RefFreq | Nominal or reference for the active power measurement. | 50 | 60 | 1 | real | Hz
12 | RefVolt | RefVolt | Reference for the active power measurement. | 220 | 240 | 1 | real | kV
13 | FreqCloseThreshold | FreqCloseThreshold | Percentage of frequcy should not be exceeded from nominal value to send the CB close command. | 1 | 5 | 1 | real | Hz
14 | VoltCloseThreshold | VoltCloseThreshold | Percentage of voltage should not be exceeded from nominal value to send the CB close command. | 1 | 5 | 1 | real | kV
15 | ActvPowDeadOpen | ActvPowDeadOpen | Active power measurement magnitude below which the CB open command to be send. | 0.0001 | 0.001 | 1 | real | kW
16 | ReactvPowDeadOpen | ReactvPowDeadOpen | Active power measurement magnitude below which the CB open command to be send. | 0.0001 | 0.001 | 1 | real | kVA
17 | PDefaultRampUpRate | PDefaultRampUpRate | Active power ramp up rate of diconnected and manual mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
18 | PDefaultRampDownRate | PDefaultRampDownRate | Active power ramp down rate of diconnected and manual mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
19 | QDeafualtRampUpRate | QDeafualtRampUpRate | Rective power ramp up rate of diconnected and manual mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
20 | QDefaultRampDownRate | QDefaultRampDownRate | Reactive power ramp down rate of diconnected and manual mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
21 | DynamicVoltWattPowRampUp | DynamicVoltWattPowRampUp | Active power ramp up rate of dynamic volt-watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
22 | DynamicVoltWattPowRampDwn | DynamicVoltWattPowRampDown | Active power ramp down rate of dynamic volt-watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
23 | DynamicVoltWattMovAvgVoltTimeWindow | DynamicVoltWattMovAvgVoltTimeWindow | Time window to calcualte moving average for dynamic volt-watt mode while charging or discharging. | 1 | 10 | 1 | real | NA
24 | DynamicVoltWattHighGradient | DynamicVoltWattHighGradient | Charging and discharging gradients while voltage exceeding the higher deadband. | 1 | 10 | 1 | real | kW/kV
25 | DynamicVoltWattLowGradient | DynamicVoltWattLowGradient | Charging and discharging gradients while voltage exceeding the lower deadband. | 1 | 10 | 1 | real | kW/kV
26 | DynamicVoltWattLowDeadBand | DynamicVoltWattLowDeadBand | Lower dead band to the differnece between moving average and nominal voltage. | 1 | 2.5 | 1 | real | kV
27 | DynamicVoltWattHighDeadBand | DynamicVoltWattHighDeadBand | Higher dead band to the differnece between moving average and nominal voltage. | 1 | 2.5 | 1 | real | kV
28 | FreqWattPowRampUp | FreqWattPowRampUp | Active power ramp up rate of auto emergency frequency watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
29 | FreqWattPowRampUp | FreqWattPowRampDown | Active power ramp down rate of auto emergency frequency watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
30 | HiStrFreq | HiStrFreq | Staritng frequency in high frequency zone. | 50.5 | 51 | 1 | real | Hz
31 | HiStpFreq | HiStpFreq | Stopping frequency in high frequency zone. | 51 | 51.5 | 1 | real | Hz
32 | HiDisChGra | HiDisChGra | Discharging gradient in the high frequency zone. | 1 | 10 | 1 | real | kW/Hz
33 | HiChGr | HiChGr | Charging gradient in the high frequnecy zone. | 1 | 10 | 1 | real | kW/Hz
34 | LoStrFreq | LoStrFreq | Staritng frequency in low frequency zone. | 1 | 10 | 1 | real | kW/Hz
35 | LoStpFreq | LoStpFreq | Stopping frequency in low frequency zone. | 1 | 10 | 1 | real | kW/Hz
36 | LoDisChGr | LoDisChGr | Discharging gradient in the low frequency zone. | 1 | 10 | 1 | real | kW/Hz
37 | LoChGr | LoChGr | Charging gradient in the low frequnecy zone. | 1 | 10 | 1 | real | kW/Hz
38 | StartDelay | StartDelay | Delay introduced for under or over frequency confirmation. | 1 | 5 | 1 | real | NA
39 | StopDelay | StopDelay | Delay introduced for restored normal frequency confirmation. | 1 | 5 | 1 | real | NA
40 | DynaminReactvCurrRampUp | DynaminReactvCurrRampUp | Reactive power ramp up rate of auto emergency dynamic reactive current mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
41 | DynaminReactvCurrRampDwn | DynaminReactvCurrRampDown | Reactive power ramp down rate of auto emergency dynamic reactive current mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
42 | DynaminReactvCurrMovAvgVoltTimeWindow | DynaminReactvCurrMovAvgVoltTimeWindow | Time window to calcualte moving average for dynamic volt-watt mode while charging or discharging. | 1 | 10 | 1 | real | NA
43 | DynaminReactvCurrVoltSagGradient | DynaminReactvCurrVoltSagGradient | Charging and discharging gradients while voltage exceeding the lower deadband. | 1 | 10 | 1 | real | kVA/kV
44 | DynaminReactvCurrVolSwellGradinet | DynaminReactvCurrVolSwellGradinet | Charging and discharging gradients while voltage exceeding the higher deadband. | 1 | 10 | 1 | real | kVA/kV
45 | DynaminReactvCurrLowDeadBand | DynaminReactvCurrLowDeadBand | Lower dead band to the differnece between moving average and nominal voltage. | 1 | 2.5 | 1 | real | kV
46 | DynaminReactvCurrHighDeadBand | DynaminReactvCurrHighDeadBand | Higher dead band to the differnece between moving average and nominal voltage. | 1 | 2.5 | 1 | real | kV
47 | ActvPowLimModeRamUp | ActvPowLimModeRamUp | Active power ramp up rate of auto normal active power limit mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
48 | ActvPowLimModeRamDown | ActvPowLimModeRamDown | Active power ramp down rate of auto normal active power limit modewhile charging or discharging. | 1 | 1000 | 1 | real | kW/min
49 | ChDischStorageModeRampUp | ChDischStorageModeRampUp | Active power ramp up rate of auto normal charge discharge storage mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
50 | ChDischStorageModeRampDown | ChDischStorageModeRampDown | Active power ramp down rate of auto normal charge discharge storage mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
51 | MinChOrDischDuration | MinChOrDischDuration | Minimum desired time for charging or discharging to reach the SoCTarget. | 1 | 100 | 1 | real | min
52 | CrdChDischModeRampUp | CrdChDischModeRampUp | Active power ramp down rate of auto normal coordinated charge discharge mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
53 | CrdChDischModeRampDown | CrdChDischModeRampDown | Active power ramp up rate of auto normal coordinated charge discharge mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
54 | MaxImportOrExportPow | MaxImportOrExportPow | Maximum imported or exported power from utility | 1 | 100000 | 1 | real | kW
55 | ReductionRatio | ReductionRatio | Reduction ratio of active power difference between ActvPowMeasRefPointPU and ActvPowMeasPU | 0 | 1 | 1 | real | NA
56 | ActvPowResponseRampUp | ActvPowResponseRampUp | Active power ramp down rate of auto normal active power response mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
57 | ActvPowResponseRampDown | ActvPowResponseRampDown | Active power ramp up rate of auto normal active power response mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
58 | VoltWattRampUp | VoltWattRampUp | Active power ramp down rate of auto normal volt watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
59 | VoltWattRampDown | VoltWattRampDown | Active power ramp up rate of auto normal volt watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
60 | VoltWatCurve (X-Y coordinates) | VoltWatCurve (X-Y coordinates) | X1 to X4 | 200 | 250 | 1 | real | kV
|  |  | Y1 to Y4 | -500 | -500 | 1 | real | kW
61 | FreqWattRampUp | FreqWattRampUp | Active power ramp down rate of auto normal frequency watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
62 | FreqWattRampDown | FreqWattRampDown | Active power ramp up rate of auto normal frequency watt mode while charging or discharging. | 1 | 1000 | 1 | real | kW/min
63 | FreqWatCurve (X-Y coordinates) | FreqWatCurve (X-Y coordinates) | X1 to X4 | 49.5 | 50.5 | 1 | real | Hz
|  |  | Y1 to Y4 | -500 | -500 | 1 | real | kW
64 | ConstVarModeRampUp | ConstVarModeRampUp | Reactive power ramp down rate of auto normal constant VAR mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
65 | ConstVarModeRampDown | ConstVarModeRampDown | Reactive power ramp up rate of auto normal constant VAR mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
66 | FxdPFModeRampUp | FxdPFModeRampUp | Reactive power ramp down rate of auto normal fixed power factor mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
67 | FxdPFModeRampDown | FxdPFModeRampDown | Reactive power ramp up rate of auto normal fixed power factor mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
68 | VoltVarModeRampUp | VoltVarModeRampUp | Reactive power ramp down rate of auto normal volt VAR mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
69 | VoltVarModeRampDown | VoltVarModeRampDown | Reactive power ramp up rate of auto normal volt VAR mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
70 | VoltVARCurve (X-Y coordinates) | VoltVARCurve (X-Y coordinates) | X1 to X4 | 200 | 250 | 1 | real | kV
|  |  | Y1 to Y4 | -500 | -500 | 1 | real | kVAR
71 | WattVarModeRampUp | WattVarModeRampUp | Reactive power ramp down rate of auto normal volt VAR mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
72 | WattVarModeRampDown | WattVarModeRampDown | Reactive power ramp up rate of auto normal volt VAR mode while charging or discharging. | 1 | 1000 | 1 | real | kVAR/min
73 | WattVARCurve (X-Y coordinates) | WattVARCurve (X-Y coordinates) | X1 to X4 | -500 | -500 | 1 | real | kW
|  |  | Y1 to Y4 | -500 | -500 | 1 | real | kW
74 | PowFactorLowerLim | PowFactorLowerLim | Power factor lower limit while lagging | -0.8 | -0.7 | 1 | real | NA
75 | PowFactorUpperLim | PowFactorUpperLim | Power factor upper limit while leading | 0.7 | 0.8 | 1 | real | NA
FreqCloseThreshold
ActvPowDeadOpenThreshold
VoltCloseThreshold
ReactvPowDeadOpenThreshold
ActvPowMeasRefPointFilterTms
EnableDispatch
PQPriority
Active pwer smoothening
Peak power limiting
Power factor coorection mode

## Input
Sl.No. | User Name | Design Name | Description | Minimum | Maximum | Scaling Factor | Data Type | Unit
1 | OperMode | OperMode | Selects the operation mode to be activated, 1,2, &3 for disconnected, manual, and auto modes. | 1 | 3 | 1 | int8 | NA
2 | SoC | SoC | State of charge measured from battery management system. | 0 | 100 | 1 | real | % (NA)
3 | TimeStep | TimeStep | Execution time step of the ESS controller. | 1 | 300 | 1 | real | ms
4 | ActvPowSet | ActvPowSet | Active power to be achieved while charging or discharing. | 0 | 1000 | 1 | real | kW
5 | ReactvPowSet | ReactvPowSet | Reactive power to be achieved while charging or discharing. | 0 | 1000 | 1 | real | kVAR
6 | ActvPowMeas | ActvPowMeas | Active power measurement from the plant electrical connection point. | -1000 | 1000 | 1 | real | kW
7 | ReactvPowMeas | ReactvPowMeas | Active power measurement from the plant electrical connection point. | -1000 | 1000 | 1 | real | kVAR
8 | FreqMeas | FreqMeas | Frequency measuremnt from the plant electrical connoction point. | 50 | 60 | 1 | real | Hz
9 | PFMeas | PFMeas | Power factor measurement from the plant electrical connection point. | -1 | 1 | 1 | real | NA
10 | VoltMeasL1 | VoltMeasL1 | Phase-a Voltage measurement at the ECP. | 127 | 139 | 1 | real | kV
11 | VoltMeasL2 | VoltMeasL2 | Phase-b Voltage measurement at the ECP. | 127 | 139 | 1 | real | kV
12 | VoltMeasL3 | VoltMeasL3 | Phase-c Voltage measurement at the ECP. | 127 | 139 | 1 | real | kV
13 | ECPCommQual | ECPCommQual | Measuements communication quality of the meter at the ECP. | 0 | 1 | 1 | Boolean | NA
14 | CBStatus | CBStatus | Circuit breaker status at the ECP. | 0 | 3 | 1 | int8 | NA
15 | CloseCmdIn | CloseCmdIn | Close command input by the user. | 0 | 1 | 1 | Boolean | NA
16 | OpenCmdIn | OpenCmdIn | Open command input by the user. | 0 | 1 | 1 | Boolean | NA
17 | SoCTarget | SoCTarget | Target SoC to be achieved in the energy storage system. | 0 | 100 | 1 | real | %(NA)
18 | PowFactorSet | PowFactorSet | Power factor to be achienved while charging and discharging. | -1 | 1 | 1 | real | NA
19 | AvgPowFactor | AvgPowFactor | Average power factor to be maintained while charging and discharging in power factor correction method. | -0.8 | 0.8 | 1 | real | NA
AutoActvPowCntrl
AutoReatcvPowCntrl

## Output
Sl.No. | User Name | Design Name | Description | Unit
1 | ActvPowOut | ActvPowOut | Active power ouput to be send from the controller. | kW
2 | ReactvPowOut | ReactvPowOut | Reactive power output to be send from the controller. | kW
3 | OpenCmd | OpenCmd | Open command output from the controller. | NA
4 | ClosCmd | CloseCmd | Close command output from the controller. | NA
5 | DynmicReatcvCurr | DynmicReatcvCurr | Reactive current output to be injected in dynamic reactive current support mode. | Amp
6 | ErrorCode | FAO | Output description6 | NA